MICHIGAN

DEPARTMENT OF TRANSPORTATION

SPECIAL PROVISION

FOR

**WATER MAIN, HIGH-DENSITY POLYETHYLENE, DIRECTIONAL BORE**

UTL:JBM 1 of 3 APPR:CJD:NJM:06-18-21

**a. Description.** This work consists of constructing an underground crossing using the horizontal directional bore method to install HDPE pipe for a proposed water main as shown on the plans. The work includes excavation, installation, backfilling, disinfection, testing, and cleanup as shown on the plans and specified herein.

**b. Submittals**. Submit product data consisting of shop drawings and manufacturer’s literature in PDF for all materials and equipment associated with the HDPE water main construction to the Engineer and the City of Croswell for approval at least 10 work days prior to construction.

Submit a general work plan outlining the procedure and schedule to be used for installation of the water main.

The Contractor may request changes to the proposed vertical and horizontal alignment of the installation and the location of the entry and exit points. Submit proposed changes in writing to the Engineer for approval, at least 10 work days prior to construction.

**c. Materials.** Provide HDPE pipe manufactured in accordance with *AWWA C906* of the size shown on the plans. Ensure that the HDPE pipe is manufactured from PE 4710 material, Pressure Class 200 psi or higher, ductile iron pipe size (DIPS), and has a Dimension Ratio (DR) of 11 or less. Furnish a manufacturer’s certification that all delivered HDPE pipe complies with the requirements of *AWWA C906*. Ensure that all HDPE pipe meets the EGLE Drinking Water & Environmental Health Division *Suggested Practice for Water Works Design, Construction and Operation for Type I Public Water Supplies.*

Ensure that the HDPE pipe is clearly marked in accordance with *AWWA C906* with the following information:

Nominal Size and Outside Diameter base

Standard Material Code Designation (PE 4710)

Standard Dimension Ratio

*AWWA* Pressure Class

*AWWA* Standard Designation Number (*AWWA C906*)

Manufacturer's identification

*National Sanitation Foundation* *(NSF)* International Standard 61 and 14 approvals

“*NSF International*-potable water” designation

**d. Construction.** Ensure that all work is in accordance with the standard specifications, and as specified herein. Install all HDPE pipe in accordance with *AWWA C906 and AWWA M55*. Ensure all permits required for the horizontal directional boring operation are coordinated and obtained by the Contractor, except the EGLE Water Main Construction Permit will be obtained by the City of Croswell.

Make HDPE pipe joints using heat fusion in accordance with *AWWA M55,* *ASTM F2620*, procedures and equipment recommended by the manufacturer and as approved by the Engineer. Accurately time the "melt" time of all joint welds. Provide to the Engineer, on request, sample joints to verify a smooth and completely "rolled" internal joint bead.

Install an annealed copper-clad steel tracer wire suitable for direct burial installation. Ensure tracer wire is 12 *AWG* copper conductor with 30-mil thick HDPE insulation, rated for 30 volts, has 21 percent conductivity and rated Extra High Strength (EHS) breaking strength. Insulation color must meet the *American Public Works Association (APWA)* color code standard for identification of buried utilities. Ensure tracer wire is in accordance with *ASTM B3, ASTM B170, ASTM D1248, ASTM D1238, ASTM B910/B910M* and the requirements of the *NEC.* Clearly label and terminate tracer wire within gate valve structures as shown on the plans. Ensure the locations of the terminations are noted on the as-built plans.

Ensure a representative from the boring contractor, who is experienced with the equipment and boring procedures, is always on site during the boring operation to address immediate concerns and emergency operations. Installation must not begin until the Engineer agrees that proper preparations have been made. Notify the Engineer at least 2 work days prior to starting the work.

Begin the directional bore with a pilot hole drilled along the proposed bore alignment. Monitor and provide directional information to the boring operator using navigation equipment on the surface. A reverse drilling reamer is attached to expand the pilot hole to allow for the HDPE pipe installation. Bentonite slurry is pumped through the drill steel where it is mixed by the reamer to stabilize and lubricate the wall lining of the bore hole and protect the HDPE pipe.

Provide and maintain instrumentation that accurately locates the pilot hole and measures drilling fluid flow and pressure at all times.

After the HDPE pipe has been installed within the bore, ensure cleaning pigs of the appropriate size are used to remove residual water and debris. The Engineer must witness and approve the cleaning.

Connections between HDPE pipe and ductile iron (DI) pipe require the utilization of an HDPE/DI transition section with stainless steel ring stiffener and a raised ring to allow for a restrained mechanical joint connection. Connections cannot be made until at least 24 hours after the HDPE pipe has been pulled through the bore hole to allow for expansion or contraction. Anchor each end of the directional bore in accordance with the flex restraint detail shown on the plans.

Contain drilling fluids within the drilling area and clean up within 48 hours following completion of HDPE pipe installation. Dispose of drilling fluid in accordance with local regulations.

Ensure deflections in HDPE pipe are made by bending the pipe in accordance with the manufacturer’s recommendations.

Restore any damage caused by heaving, settlement, escaping drilling fluid (frac-out), or the drilling setup and operation. Ensure a frac-out contingency plan is provided and approved by the Engineer prior to starting the work.

If an obstruction is encountered during the boring operation that prevents completion of the installation in accordance with the design location and specification, the HDPE pipe may be abandoned and left in place with approval of the Engineer. If the HDPE pipe is approved to be left in place, ensure it is immediately filled with flowable fill and bulkheaded. Submit a revised plan prior to beginning another boring for approval by the Engineer. If, during construction, damage is observed, cease all work until a plan to minimize further damage and for restoration is obtained and approved by the Engineer.

If conditions warrant removal of any materials installed in a failed bore path, as determined by the Engineer, it will be at no additional cost to the contract.

Hydrostatic testing, disinfection, and water analyses of all water main installed by the Contractor are required. Ensure hydrostatic testing, disinfection, and water analyses is coordinated with other water main work and is performed in accordance with current *AWWA* standards and the standard specifications, except that the HDPE pressure test must include an initial expansion phase prior to testing, allowable leakage is zero, and disinfecting solutions must not exceed 12 percent active chlorine in accordance with the *Plastics Pipe Institute “Handbook of Polyethylene Pipe”* and *AWWA Manual M55*. Ensure water samples are collected at each branch, every 1200 feet, and at the pipe installation ends per *AWWA C651*.

Provide the Engineer a complete set of as-built plans, showing all bores (successful and failed), within 30 calendar days of completing the work. Ensure as-built plans include the locating equipment used; horizontal and vertical alignment with degree of accuracy, entry, and exit points; bore diameter; tracer wire termination locations; drilling fluid composition; and important subsurface features. Ensure the as-built plans are legibly drawn on project plan sheets or sheets developed by the boring contractor. The Engineer will have 15 calendar days to review and approve the as-built plans.

**e. Measurement and Payment.** The completed work, as described, will be measured and paid for at the contract unit price using the following pay item:

**Pay Item** **Pay Unit**

Water Main, HDPE, \_\_ inch, Directional Bore Foot

**Water Main, HDPE, \_\_ inch, Directional Bore** will be measured horizontally from bore entrance to bore exit with no allowance for curvature of the pipe. This item includes all utility location, excavation, backfill, boring, flowable fill, connections and flex restraint, tracer wire, monument boxes, grouting around the HDPE pipe, sheeting and bracing, dewatering, testing, disinfection and flushing, cleanup, disposal, as-built plans, and all other miscellaneous items of work necessary to complete the bore and install the HDPE pipe.

No payment will be made for directional boring until as-built plans have been reviewed and approved by the Engineer.