MICHIGAN

DEPARTMENT OF TRANSPORTATION

SPECIAL PROVISION

FOR

**PUMP STATION EQUIPMENT, ELECTRICAL**

DET:SP 1 of 6 APPR:RPB:NJM:06-13-23

**a. Description.** This work consists of furnishing and installing the pump station electrical equipment as shown on the plans, in this special provision, and as directed by the Engineer. Follow industry standards and in accordance with the details shown on the plans.

**b. Materials.** Furnish new materials that meet the standards and practices of the *NEC, ANSI, ASTM, UL, NEMA*, the standard specifications, *MIOSHA*, and this special provision.

Ensure all electrical devices furnished under this contract are new and are received at the job site in the manufacturer’s shipping container that clearly identifies the items. Used, rebuilt, or discontinued models are prohibited for installation under this contract unless otherwise specifically noted on the plans.

Ensure all components installed in hazardous areas shown on the plans are explosion proof or intrinsically safe as outlined in the *NEC*.

1. Conduit and Fittings. Furnish PVC-coated rigid steel for all exposed conduit and fittings in the pump station and all exposed exterior conduit and fittings. Ensure couplings and connectors are threaded type. Ensure outdoor buried conduit is Schedule 80 PVC with PVC-coated rigid steel sweeps.

Ensure conduit terminations consists of double locknuts and insulated bushings, wet location connectors, or threaded hubs as applicable to maintain the ratings of the enclosure to which it is being terminated.

Ensure all joints in conduits are made with standard couplings unless neither conduit can be turned; then, ensure the union is made with a threaded rigid split coupling or three-piece couplings. Running threads is prohibited.

Furnish flexible liquid tight metal conduit for connections to vibrating or rotating equipment listed and appropriately labeled by a nationally recognized testing laboratory (NRTL) as conforming to applicable *UL* standards.

Flexible steel conduit is prohibited.

2. Wire and Cable. Ensure indoor feeder circuit, branch circuit, and control circuit wiring is stranded copper, 600 volt (V) insulation, *UL* Type “THW”, “THWN”, or “XHHW” moisture and heat resistant thermoplastic approved by the *NEC* for operating temperature of 75 ºC and for installation in wet or dry locations.

Use *UL* Type “XHHW” heat resistant wire when wiring between fixtures and their adjacent outlets.

Use single conductor stranded copper cable that has corona, ozone, heat, and moisture resistant cross-linked polyethylene 600 V insulation, or approved equal, rated to withstand a copper temperature of 90 ºC without deterioration for 480 V standards service. Ensure cable meets applicable *ICEA Standards* and is NRTL labeled, *UL* type “XHHW”.

Ensure all wire and cable, including feeders, main, and branch circuits, is color coded as follows:

480/277 V

Color Phase

Brown A

Orange B

Yellow C

Gray Neutral

Green Ground

Ensure conductors No. 8 and smaller have color coded insulation. Ensure conductors No. 6 and larger have terminations and conductors in pull boxes taped with colored tape, not less than two inches wide.

3. Pull Boxes. Furnish pull boxes, junction boxes, and cable support boxes of proper size and design in accordance with the *NEC* and as required to facilitate installation of wires. Ensure covers are gasketed and held in place with corrosion-resistant machine screws. Furnish cable supports for vertical runs at code required locations, with pull or junction boxes. Ensure boxes are *NEMA 4X* stainless steel construction or *NEMA 7* where shown on the plans.

4. Wiring Devices. Ensure wiring devices (switches, receptacles, and other such appurtenances) are rated for 20 Amperes (A) at 120 VAC unless otherwise shown on the plans.

5. Outlet Boxes. Ensure outlet boxes for exposed work are of PVC-coated steel construction with threaded shallow depth ferrous box (*UL* Type “FS”) openings unless otherwise shown on the plans.

6. Lighting Fixtures. Furnish light fixture types, as specified in the lighting fixture schedule on the plans, that are complete, including all power supplies, drivers, fuses, support brackets, and other parts and devices necessary for complete operation. Ensure lighting fixtures utilize LEDs as the light source and operate on 120 V as shown on the plans. Furnish LEDs of the color temperature as follows: 5,000 kelvin (K) (±500K) for the Machine Room, 5,000K (±500K) for the Rake Room, and 4,000K (±500K) for all other spaces. LED luminaires must have a minimum 100,000-hour rating for 70 percent lumen-depreciation (minimum) with lumen output within 20 percent of listed fixture. Clean all fixtures at the end of the project.

7. Distribution Panelboards. Furnish distribution panels of code grade gauge stainless steel of the dead front safety type with 35,000 A interrupting capacity (AIC) single or multi-pole circuit breaker branches of the number and ampere rating as shown on the plans. Ensure the main panel bus is copper. Furnish bolt-on breakers. Fabricate distribution panel enclosures in sections not exceeding 36 inches in width and 18 inches in depth.

8. Lighting Transformer. Furnish 480 V primary with 240/120 V single phase secondary. Ensure the transformer is rated for 115 ºC temperature rise above 40 ºC ambient. Ensure all insulating materials are in accordance with *NEMA ST20 standards*. Ensure the transformer is in a heavy-duty stainless steel waterproof enclosure. Design the transformer to be either floor or wall mounted.

9. Branch Circuit Panelboards. Furnish branch circuit panelboards of code grade gauge stainless steel, dead front safety type with 22,000 AIC single or multi-pole circuit breaker, with branches of the number and ampere rating as shown on the plans. Ensure the main bus is copper. Furnish bolt-on breakers only. Fabricate distribution panel enclosures in sections not exceeding 36 inches in width and 6 inches in depth.

Ensure panels have a main circuit breaker as shown on the plans and have 22,000 Root Mean Square (RMS) symmetrical interrupting capacity for 120/240 V panels.

10. Receptacles. Furnish receptacles that are a duplex convenience ground type, unless otherwise specified, with weather tight gasket and covers, and install in exposed cast conduit standard depth ferrous boxes (*UL* Type “FD”) with metal mounting ears. This includes receptacles used for disconnects.

Ensure convenience receptacles are rated 20 A with back and side wiring and with exposed metal parts finished to resist corrosion.

Ensure special purpose receptacles are rated 20 A, 230 V, unless otherwise called for on the plans.

Ensure receptacles have a wet location, cast-metal spring type cover for each receptacle mounted on an *UL* Type “FS” and *UL* Type “FD” box.

11. Light Switches. Ensure switches are *UL* “T” rated. Ensure switches and receptacles are heavy duty, specification grade, and as called for on the plans.

Ensure device covers are listed for wet location, cast metal, for *UL* Type “FD” box application, unless otherwise called for on the plans.

12. Grounding and Bonding. Ensure ground rod electrodes are of copper-clad material, 3/4-inch diameter, and a minimum of 10 feet in length. Ensure the motor frames, control cabinet, conduits, and all noncurrent carrying metal parts of all electrical equipment are securely grounded to the ground cable. Ensure grounding cables are attached to equipment with solderless ground lugs, bolts and nuts or machine screws.

13. Supporting Devices. Ensure support systems can support the weight of said equipment, conduit, and wiring.

Ensure fastening equipment is of stainless-steel construction. Ensure all channel strut and fastening products are of stainless-steel construction.

14. Transient Voltage Surge Suppressors (TVSS). Ensure the main electrical distribution panelboard and the branch circuit panelboard are protected with a TVSS device that meets the requirements of *ANSI/UL 1449* and *ANSI/IEEE C.62.41-1980* and provided with a fused or circuit breaker disconnecting means. Ensure the units are rated 600 V, 100 kiloampere (kA) per phase, Line-to-Line, Line-to-Neutral, and Line-to-Ground.

15. Motor Starters. Furnish combination type, three phase, *NEMA* rated single speed, non-reversing, across the line, magnetic type motor starters with NEMA 4 stainless steel enclosure, *NEMA* size 1 minimum. Furnish two spare auxiliary contacts in addition to those used in the pump control circuit. Furnish starters with melting alloy type thermal overload relays. Refer to wiring diagrams for specific details.

16. Pump Control Panel. Existing panel(s) to remain. Protect panel and all associated controls during construction. The control panel will need to be reprogrammed prior to completion of the project. Ensure the reprogramming and resetting of controls is completed by an authorized representative of the controls/Supervisory Control and Data Acquisition (SCADA) system and the representative is located in Michigan.

17. Conduit to Wall Penetration Seals. Furnish seals with interlocking, bolted rubber links shaped to the annular space between the pipe and the concrete cored opening. Furnish the size and number of rubber links to suit the pipe outside diameter and sleeve, as recommended by the manufacturer. Ensure all hardware is stainless steel.

18. Disconnect and reconnect the existing level probe as shown on the plans. The level probe is a submersible hydrostatic-type level transducer constructed with a welded 316 stainless steel with a Teflon-coated elastomeric diaphragm. Probe output is a 4-20 mA DC signal, is 2-wire, loop powered, and includes intrinsically safe barriers.

19. Disconnect and reconnect the existing float switches. Float switches are Teflon coated, stainless steel, direct acting type, approximately five inches in diameter with potted single-pole double-throw (SPDT) mercury contact switch, narrow activation range.

20. Caution Tag. Ensure each panel receiving power from a separate source, which is not disconnected by the primary disconnect means, has a laminated orange tag 3-inches wide by 1.5-inches high with 3/8-inch-high white lettering reading: “CAUTION - SEPARATE VOLTAGE SOURCE.”

21. Nameplates. Ensure nameplates for safety switches, lighting panels, starter enclosures, panelboards, etc., are laminated white plastic with black lettering and are attached with sheet metal screws. Ensure nameplates are 2½-inches by 3/4-inches. Ensure the first line character size is 1/4-inches high and the second line 3/16-inches high. Ensure all panelboards include the final typed circuit directory installed inside of cover.

Ensure field located instruments and devices are equipped and identified with 1-inch by 3-inch engraved nameplates (similar to panelboard nameplate) and affixed to their respective device in a positive but flexible method (wire strap or similar means).

22. Fans and Motors. Fans must provide air flow capability as shown on the plans. Ensure all fan motors are explosion-proof. Ensure the fan is *Air Movement and Control Association (AMCA)* “B” rated and equipped with aluminum fan wheels. Ensure fan shrouds, motor and fan wheel are removable for service. Furnish *MIOSHA* approved guards. Ensure fan is automatically controlled as shown in the wiring diagram.

23. Electric Unit Heaters. Ensure electric unit heater furnishes minimum heating capacity as shown on plans. Furnish explosion-proof style, epoxy-coated steel case, *NRTL* listed as meeting *UL* requirements, aluminized steel tubular elements, explosion-proof motor, explosion-proof, gasketed electrical enclosure, high limit safety, integral thermostat, and stainless-steel universal mounting bracket.

24. Mixes. Ensure patches, conduit sealing compound, fire stop compound, etc., are mixed in accordance with the manufacturer’s recommendations.

**c. Construction.** Ensure all work meets the standards and practices of the *NEC, ANSI*, the standard specifications, *MIOSHA*, and this special provision. Ensure all electrical work is done by a licensed electrician and in accordance with the *NEC*. Electronically submit a copy of the license to the Engineer.

Construct and install all materials and components at the locations shown on the plans unless otherwise approved by the Engineer.

Field verify and document the existing pump operation level prior to construction. Ensure reconnected float switches and sequences of operation match the information shown on the plans.

Furnish temporary seals on outlet boxes during construction.

Preassemble, to the degree possible, panelboards, control panels, relay panels, etc. This preassembly should be done offsite in a clean shop environment by the Contractor or manufacturer. Configure equipment to fit through the hatch size shown on the plans.

Ensure all wire and cable is continuous in the same color code and type to its extreme termination point. The use of different type of insulated wire to the same device or equipment is prohibited.

Install electrical grounding system in accordance with *NEC* requirements. Measure grounding system resistance using the “fall of potential” method. Ensure this test is witnessed by the Engineer, with the final test results electronically submitted to the Engineer for final approval.

Install support systems that are adequate for the weight of equipment, conduit, and associated wiring. Ensure support devices are not fastened to piping, ductwork, mechanical equipment, or conduit.

Install surface mounted cabinets and panelboards with a minimum of four anchors. Furnish stainless-steel channel supports to stand cabinet one inch off the wall. All freestanding electrical equipment is to be installed on a raised, six-inch reinforced concrete pad.

Furnish wire markers on each conductor in panelboard or pump control cabinet gutters, pull boxes, outlets, junction boxes, and load connection. Identify branch circuit and feeder number for power and lighting circuits and with control wire number as identified on the schematic and interconnection diagrams for control wiring. Ensure wire markers are preprinted and not pieced from single and/or double-digit tags. Embossed tape is prohibited for any application.

Furnish an electrical system Short Circuit and Arc Flash hazard study in accordance with National Fire Protection Association (*NFPA) 70E, OSHA 29-CRF, part 1910 Sub-part S,* and *IEEE 1584 standard*. Upon acceptance of the study, furnish and install on the appropriate equipment, preprinted, adhesive-backed arc-flash warning labels that incorporate the information in subsection c.2 of this special provision. Ensure the study addresses the following:

1. The available short circuit and ground fault currents available at each bus. Incorporate the motor contribution in determining the momentary and interrupting ratings of the protective devices.

2. The flash hazard protection boundary, limited approach boundary, restricted boundary, prohibited boundary, incident energy level, required personal protective equipment class, and type of fire-rated clothing required.

Submittals. When directed by the Engineer or required by the specifications, submit samples of materials and accessory equipment such as light fixtures, switches, receptacles, etc. Do not use these materials in the work until the Engineer has had ample time to determine the products’ suitability and compliance with the specifications. Ensure all submittals are an electronic PDF document. Allow 15 working days for shop drawing reviews. Electronically submit the following information for approval by the Engineer.

3. Catalog cuts and/or product data sheets. Furnish catalog cuts for standard manufactured items such as conduit and conduit fittings, electric heaters, fans, light fixtures, lighting panels, instrument motors, switches, disconnects, transformers, wire, etc. Ensure each sheet identifies the exact equipment for which it is intended. Ensure all pertinent information such as physical dimensions, current rating, horsepower, kilowatt rating, phase, power factor, voltage, *NEMA* classifications, and material type used are labeled with an *NRTL* listing identification.

4. Schedule. Electronically submit a schedule that outlines the steps to be taken to maintain electrical service and showing the coordination effort which will be taken to coordinate the work between the various trades.

The approval of shop drawings does not relieve the Contractor from the responsibility to correct errors or omissions or to furnish adequate field measurements and quantities of materials that may be required. It is the Contractor’s responsibility to call attention to all deviations from the plans, specifications, and details. If deviations have not been clearly identified, they will not be considered as part of the shop drawing approval.

**d. Measurement and Payment.** The completed work, as described, will be measured as a lump sum and paid for at the contract price using the following pay item:

**Pay Item Pay Unit**

Pump Station Equipment, Elec (Structure Identification) Lump Sum