MICHIGAN

DEPARTMENT OF TRANSPORTATION

SPECIAL PROVISION

FOR

CURED-IN-PLACE PIPE POINT REPAIR

ISH:JSK	1 of 2	APPR:DMG:MLO:02-17-23

a.	Description.  This work consists of the design and installation of cured-in-place fiberglass point repairs on existing storm sewer pipe.  Repair storm sewers at the locations shown on the plans and in accordance with the standard specifications, the manufacturer’s installation guidelines and as specified.

Provide video inspection of sewers before (after cleaning) and after point repairs have been made.  All sewer cleaning, disposal, maintaining flow, bypass pumping, corrective action to remove obstructions, site preparation and restoration is included in this work except as described below.

b.	Materials.  Use a fiberglass point repair sleeve by PipePatch® manufactured by Source One Environmental or approved equal meeting the minimum requirements of ASTM F1216.

c.	Construction.  Provide at least 10 work days notice to the Engineer prior to starting the work.  Electronically submit all required documentation to the Engineer for approval prior to starting the work.  Do not begin work until approval is received from the Engineer.

Video inspect the existing pipe in accordance with subsection 402.03.J of the Standard Specifications for Construction.  Thoroughly clean the existing pipe prior to video inspection.  Dispose of all debris in accordance with subsection 205.03.P of the Standard Specifications for Construction.

Propose corrective action to eliminate any obstruction revealed by the pre-installation inspection that cannot be removed by conventional pipe cleaning equipment and that prevents the point repair from being installed properly.  Ensure the proposed corrective action is approved by the Engineer prior to commencement of the work.

Maintain flow around the run of pipe designated for pipe point repair as necessary.  Ensure the bypass pumping system can provide adequate capacity to handle the existing flow plus any additional flow that may occur during periods of precipitation.  Electronically submit a bypass pumping plan containing all necessary details to the Engineer for approval at least 10 work days prior to conducting the work.  Continuously monitor all pumps and equipment.  Follow local noise ordinances if pumping is required on a 24-hour basis.

Install the fiberglass patch in accordance with the manufacturer’s published guidelines.  Ensure the finished fiberglass patch covers the entire length of pipe defect and is free from visual defects.  Upon completion of the installation of the patch provide video inspection of all repaired locations.  Correct any deficiencies found at no cost to the contract utilizing a method approved by the Engineer.

Any areas found to be defective with the patch or between the patch and the existing pipe as determined by the Engineer may require grout or other corrective action.  Conduct the work in accordance with the manufacturer’s guidelines to ensure a quality repair to minimize irregularities in the patch or eliminate groundwater infiltration.

Provide a certification, sealed by a Professional Engineer licensed in the State of Michigan, verifying that the point repair patch system has been designed, manufactured, and installed in accordance with ASTM F1216 and this special provision.

d.	Measurement and Payment.  The completed work, as described, will be measured and paid for at the contract unit price using the following pay item:

Pay Item	Pay Unit

Cured-In-Place Pipe Point Repr, __ inch	Foot

Cured-In-Place Pipe, Point Repr, __ inch includes cleaning, debris disposal, patch installation and video inspection necessary to repair the sewer pipe as described.

The cost for the work to remove an obstruction that cannot be removed with conventional pipe cleaning equipment will be paid for separately in accordance with the contract.