MICHIGAN

DEPARTMENT OF TRANSPORTION

SPECIAL PROVISION

FOR

WATER MAIN INSTALLATION

DAV:DJM	1 of 6	APPR:RPB:CJD:05-13-24

a.	Description.  This work consists of installing water main and appurtenances in accordance with the plans, this special provision, AWWA, EGLE, and the standard specifications.  The city of Owosso (City) Department of Public Works can assist the Contractor in locating existing water service leads and mains.  Ensure all removed valves and hydrants are salvaged and returned to the Department of Public Works.  The Contractor must contact the Engineer to schedule work interfering with existing water service.  The City Department of Public Services must approve any temporary shut off of service.

b.	Submittals.  Submit product data in PDF form consisting of shop drawings and manufacturer’s literature to the Engineer and the City for approval at least 10 working days prior to construction.

Submit a general work plan outlining the procedure and schedule to be used for installation of the water main and associated appurtenances.

c.	Materials.  Furnish new materials meeting minimum specifications of AWWA Standards, the standard specifications, and the City specifications.  Ensure materials are lead-free as defined by the United States Environmental Protection Agency Safe Drinking Water Act, in that; “All pipes, pipe fittings, plumbing fittings, and fixtures that are used for potable water must comply with the lead free requirement and must bear the mark National Sanitation Foundation (NSF)/ANSI Standard 61, Annex G or NSF 61-G.”

1.	Pipe.  Furnish DI pipe in accordance with AWWA C151/C600 for open-cut, jack and bore, or when attached to a bridge structure.  DI pipe must meet Thickness Class 52 and Pressure Class 350.  Ensure DI pipe is lined with a cement mortar and bituminous seal coat in accordance with AWWA C104.  Ensure manufacturer and class are marked on each length of pipe.

2.	Poly Wrap.  Pipe, fittings, joints, and fire hydrants in soils contaminated with volatile organic compounds, as determined in the field by the Engineer, must use Linear Low-Density Polyethylene black (8-mil) Poly Wrap ANSI/AWWA C105/A21.5, ASTM D882, to within one foot of finished grade.

3.	Fittings/Joints.  Ensure joints are push-on type with elastomeric gaskets meeting the requirements of ASTM D3139/F477 or AWWA C111 and are furnished with an electrical conductivity device.  Ensure fittings are cast iron or DI with mechanical joints and in accordance with AWWA C153/ANSI A21.53.  Ensure fittings are cement-lined in accordance with ANSI/AWWA A21.4/C104 and rated for 250 psi or more.  Following manufacturer’s standards, mechanical joint restraint are required and must be MEGALUG by EBAA Iron.  All mechanical joints and fittings requiring bolt-on fasteners must use blue fluoropolymer coated fasteners.  Corrosion protective material as a barrier encasement in varying soil conditions is required.  Use Linear Low-Density Polyethylene black (8-mil) Poly Wrap ANSI/AWWA C105/A21.5 ASTM D882, or Sanchem, Inc. NO-OXG-ID GG-2 lubricant.  Corotech coal tar epoxy is not permitted for use.  DI water main requires the use of nitrile gaskets where hazardous soils exist.

4.	Fire Hydrants.  Install entire hydrant assembly as shown on the plans.  Extensions will not be paid for separately.  Furnish fire hydrants as manufactured by East Jordan (EJ) Storz 5BR250 with 5½-foot depth of bury in accordance with AWWA C502.  Ensure hydrants are dry-barrel, fire hydrant traffic model or traffic flange type, 150 psi working pressure, compression type, opening with line pressure, with mechanical joints.  Ensure iron parts are of high-strength grey iron in accordance with ASTM A126 Class B.  Fire hydrants must have a 6-inch valve opening with a 6-inch mechanical joint inlet.  Ensure the minimum inside dimension is eight inches.  The operating nut must turn to the right to open.  Ensure the opening direction is plainly marked with an arrow near the operating nut showing the opening direction.  Ensure the operating nuts and nut nozzle caps are square and slightly tapered and be 15/16-inch at its base and 13/16-inch square at its end and 1⅛-inch long.  Completely assemble fire hydrants at the factory with the drain opening sealed with a threaded plug.  Furnish two fire hose connections and one pumper connection in accordance with City standards.  Ensure nozzles are on a movable head on the hydrant barrel so that they may be rotated by changing the position of the top flange without removing the barrel.  Furnish proper length for installation at water main depth as shown on the drawings.  Paint fire hydrants yellow above the grade line and black below the grade line.  Ensure the 5-inch cap is painted to AWWA color code based on City gallons per minute (GPM) flow data.  Design fire hydrants so one man can easily remove or replace the working parts without removing the main valve seat.  Fire hydrants flags are optional and only upon request of City.

5.	Gate Valves.  Furnish gate valves as manufactured by East Jordan (EJ).  Ensure valves for use in water distribution systems are resilient seat, single wedge valves in accordance with AWWA C509 and must also meet any supplemental requirements of the City.  Valves must have mechanical joints with stainless steel bolts.  Ensure the valves are manually operated with non-rising stems, iron body, bronze trim.  Furnish valves with a standard AWWA 2-inch square-operating nut.  The wrench nut must turn right (clockwise) to open with red top and must be shown by an arrow cast on the operating nut skirt.  Valve stem risers are required for depths greater than 6-feet-6-inch and will not be paid for separately.

6.	Valve boxes.  Furnish valve boxes manufactured by EJ.  Ensure the valve box is cast iron, 5½-inch diameter, and three-piece adjustable screw type.  Valve box extensions are required for depths greater than 6-feet-6-inch and will not be paid for separately.  Number 6 round bases are required for gate valves up to 8-inches in diameter.  Number 160 oval bases for gate valves 10-inches and greater.  Ensure the drop covers are stamped “WATER”.

7.	Water services.  Ensure the water service piping is copper tubing, Type K, annealed, in accordance with ASTM B88.  The size of tubing must match the existing size of the water service being replaced.  Ensure the fittings are in accordance with ASME B16.26, cast bronze.  Use compression type joints for the copper tubing.  All water services are to be constructed at 90 degrees from water main to curb-stop/meter pit.

8.	Water Service taps made on DI Pipe.  For 1-inch residential service tap, no saddle is required.  Use Ford #F-1000-4-Q-NL.  For larger than 1-inch service tap, use Ford #F series as appropriate.

9.	Curb stop boxes.  Use 3/4-inch ball stops manufactured by Ford, Model #B-44-333-Q-NL.  Use 1-inch ball stops manufactured by Ford, Model #B-44-444-Q-NL.  Female thread x copper tube size quick joint (CTS QJ) or CTS QJ x CTS QJ.  Ensure curb stops are 5-feet 6-inches deep.  Ensure curb stop boxes are the Standard Buffalo pattern and all parts of the same, including extension sections, are interchangeable and fit up with corresponding parts of other Standard Buffalo pattern boxes.  Ensure internal diameter of base shaft is 2½ inches for 3/4-inch and 1-inch curb stop.  Use cast iron boxes, suitably coated to resist corrosion with the casting smooth and free of any imperfections.  The covers must overlap, fit outside the rim of the upper section, and have a horseshoe-shaped groove to receive the bolt head and the word “WATER” embossed on the top surface.  Ensure all boxes are Tyler 6500 (2½-inch boxes) Series.

10.	Tracer Wire.  Ensure tracer wire is #10 AWG polyethylene coated steel core copper wire, attached to pipe by tape or other approved means.  Use tracer wire manufactured by Copperhead Industries, LLC – Copperhead Reinforced Tracer Wire, or equal.  Tracer wire connectors must contain a dielectric waterproof and corrosion proof sealant, lock shut, and be color coded blue.  Ensure all ends are terminated into approved tracer wire box.  Ensure tracer wire is not installed inside the valve box.

11.	Tracer Wire Boxes.  Ensure tracer wire boxes are magnetized with a direct connection to tracer wire without removing the cover, be color coded, and have a locking cover.  Install tracer wire boxes at every fire hydrant, isolation valve (separate from the valve riser), and at every distribution water main isolation valve (separate from the valve riser).  Ensure tracer wire boxes are color coded blue and Copperhead Industries, LLC – Snake-Pit Magnetized Tracer Box, or equal.  Install tracer wire box between hydrant and hydrant valve.

12.	Air Release Well.  Build air release well as shown on the plans and in accordance with section 403 of the Standard Specification for Construction.  Mix mortar for masonry work in quantities that will be used before initial set.  Do not use mortar that requires retempering.  Position the air release valve to allow access through the opening in the manhole.  Construct wells to allow minor valve repairs.  Protect the valve and pipe from impact where passing through the well walls.

13.	Water Main Bridge.  Install water main under the bridge in full manufactured pipe lengths and insulated using the two-fill GF Urecon, UIP® factory insulation process, or equal.  Ensure the insulation of associated joints, fittings, and accessories are per manufacturer’s instructions.

A.	Insulation.  Factory applied rigid polyurethane foam must have the following properties.  Insulation Thickness:  nominal 2.5 inches.  Insulation Density:  ASTM D1622, 2.2 to 2.81 pcf.  Insulation Closed Cell Content:  ASTM D6226, 90 percent or greater.  Insulation Water Absorption:  ASTM D2842, 4.0 percent or greater by volume.  Insulation Thermal conductivity:  ASTM C518, 0.14 to 0.154 Btu x inch/square foot x hour x °F.

(1)	System.  System compressive strength:  (modified ASTM D1621) approximately 200 psi.  Service temperature range:  the overall factory insulated system limitations are dependent on the core pipe type, insulation, and application.  Temperature limitation:  minimum ambient installation temperature -29 °F.

(2)	Outer Jacket.  Locked seam, spiral wound round metal jacket.  Galvanized steel:  Insulated jacket outside diameter less than or equal to 18 inch at 22 gauge.

(3)	Insulated pipe joints.  Bell x spigot joints.  Ensure insulated pipe joints with no mechanical restraints are sealed with 6-inch-wide metal wraps consistent with that on the factory insulated pipe complete with stainless steel bands and gear clamps, depending on pipe size.

(4)	Insulation kits for fittings.  Insulation kits for fittings must consist of rigid polyisocyanurate or polyurethane foam half shells complete with a thin polymer coating on all surfaces for strength during transit and installation, and fabricated metal cover consistent with that on the factory-insulated pipe.  All insulation kits to be supplied complete with stainless steel bands and gear clamps.

(5)	Rigid polyisocyanurate or polyurethane foam.  Density: ASTM D1622, 2.0 pcf.  Compressive strength:  ASTM D1621, 18 to 27 pounds per inch squared.  Closed cell content:  ASTM D6226, 90 percent minimum.  Water absorption:  ASTM C272/C272M, 2.0 perccent by volume.  K factor:  ASTM C518, 0.19 BTU x inches per square foot x hour x °F.  Thickness:  Typically, 2 inch, other thicknesses upon request, must match pipe insulation thickness.

(6)	Polymer coating, GF Urecon BL-20-20EP, or equal.  Two component high density polyurethane coating, black in color.  Density:  73 pcf.  Durometer D scale 60.  Tensile strength:  1610 pounds per square inch.  Tear strength:  151 pounds per inch.  Thickness:  20 mils outside surfaces, 20 mils inside surfaces.

14.	Water Main Bridge Support.  Furnish a pipe support system for the water main bridge crossing utilizing adjustable support rollers (cast iron pipe roll, cast iron sockets, carbon steel roll rod, threaded rods, and adjustment nuts) and stainless-steel U strap clamp as shown on the plans.

d.	Construction.

1.	Jointing.  Install mechanical joints in accordance with the joint manufacturer's recommendations per joint restraint schedule as shown on the plans.  Furnish copies of such recommendations to the Engineer prior to the start of construction.

2.	Thrust Blocking.  Install thrust blocks at tees, 90-degree bends, and at dead end water mains in accordance with section 823 of the Standard Specifications for Construction and as shown on the plans.  Ensure all tees and 90-degree bends, and other fittings subjected to unequal thrust are restrained using mechanical joint fittings with retainer glands on both sides of the bend or tee and must also be supported with thrust blocking.  Ensure all 45-degree bends and thrust blocking are restrained with MEGALUG fittings.  Use 90-degree bends only if 45-degree bends cannot be used due to limited space.

3.	Hydrants.  Locate hydrants as shown on the plans and approved by the City.  Ensure use of bends in connections are approved by Engineer and the City.

4.	Valves.  Install valves with the valve closed, supported on two 2-inch by 6-inch by 18-inch hardwood blocks.  Valve boxes must have the ability for future adjustments of up to 6 inches above or below grade.

5.	Water.  A service charge of $1,000 will be required at the time of permit application.  This fee includes the minimum charge of $60 for 5,000 bulk gallons of water, plus additional charges of $12 per 1,000 gallons consumed in excess of the minimum quantity.  Owosso Water System personnel will attach a water meter and Reduced Pressure Zone (RPZ) backflow preventer to the hydrant for Contractor use.  If the water meter and RPZ is returned in good operating condition, the Contractor will receive a $450 refund, less additional water consumed in excess of minimum quantity.

6.	Pipe Support.  Install the pipe support system as shown on the plans per the manufacturer’s recommendations.  Install one hanger per pipe section immediately behind the bell (the bell should not rest on the floor) at structural steel hanger locations.

7.	Water Services.  Use open cut method to install water services.

e.	Sterilization.

1.	Preliminary Flushing.  Flush the main prior to sterilization as thoroughly as possible with water pressure and outlets available.  Ensure the minimum velocity in the main is 3.0 feet per second.  Ensure the flushing operation is done after the pressure test has been made.  A service charge of $1,000 will be required at the time of permit application.  This fee includes the minimum charge of $60 for 5,000 bulk gallons of water, plus additional charges of $12 per 1,000 gallons consumed in excess of the minimum quantity.  Owosso Water System personnel will attach a water meter and RPZ backflow preventer to the hydrant for Contractor use.  If the water meter and RPZ is returned in good operating condition, the Contractor will receive a $450 refund, less additional water consumed in excess of minimum quantity.

2.	Notification to Residents of Water Service Shutdowns.  The City Engineer or designated representative must notify Contractor of successful water sampling and testing acceptance for connecting to potable water system.  The Director of Public Services must give notice to proceed with connection to potable water system.  After receiving Notice to Proceed, the Contractor must give a minimum 48-hour notice of planned water supply shut off for connection to potable water system.  City will determine affected area of planned water supply service interruption and send out notices 24 hours prior to planned water service interruption.  Prior to planned water supply shut off, the Contractor must have performed a thorough investigation and review of necessary parts and components adequately sized and available on site at time of connection to the potable water supply to avoid unnecessary lengthy water service interruptions to residents and businesses.

f.	Measurement and Payment.  The completed work, as described, will be measured and paid for at the contract unit price using the following pay item:

Pay Item	Pay Unit

Water Main, DI, __ inch, Bridge	Foot

Air Release Well, __ inch	Each

Water Main, Bridge Support Assembly 	Each

1.	Water Main, DI, __ inch, Bridge of the size required will be measured along the centerline of the pipe from beginning of bridge to end of bridge.  Water Main, DI, __ inch, Bridge includes the cost of the following:  furnishing and installing fittings and gaskets, bracing or sheeting, blocking, pipe insulation and outer jacket; pipe to bridge attachment straps and anchors; and preparing and furnsihing as-built plans.

2.	Air Release Well, __ inch will be measured per each installed.  Air Release Well, __ inch includes the cost of the following: concrete footing; concrete structure; temporary and final adjustments of the structure; structure casting, frame, and cover; steel restraint plate, sewer outlet pipe and non-shrink grout; corporation stop; required fittings and blocking; abutment wall coring for outlet pipe; and all material, labor, and equipment necessary for a complete installation.

Water main pipe installed inside the Air Release Well will be paid for as Water Main, DI, __ inch, Bridge.

3.	Water Main, Bridge Support Assembly includes furnishing and installing the adjustable support rollers (cast iron pipe roll, cast iron sockets, carbon steel roll rod, threaded rods, and adjustable nuts) and stainless-steel U strap clamp as shown on the plans.